## Slide 1: Greening Multi-Tenant Data Center Demand Response
Niangjun Chen
Joint work with Xiaoqi Ren, Shaolei Ren, and Adam Wierman
Notes: ----- Meeting Notes (10/9/15 11:49) -----
thanks for the introduction, today I will be talking about how to do demand response for multi-tenant data center efficiently, and how can we make it more environmentally friendly

## Slide 2: 2 stories about energy and data centers
Emerging story: data centers are valuable resources
Typical story: data centers are energy hogs
Idea: use data centers for demand response (DR)
Notes: ----- Meeting Notes (10/16/15 13:52) -----
data center has flexibility in terms of power consumption, ... virtual battery ... (flexibility can be valuable for demand response)

## Slide 3: DR is crucial for renewable integration
demand
generation
DR
Notes: ----- Meeting Notes (10/16/15 13:52) -----
on the generation side, they can use large scale storage to deal with the (renewable), but really expensive ...

## Slide 4: Finding DR resources is challenging
GTM research, “U.S. Demand Response Outlook 2014”
Conservative
estimate
Aggressive
estimate
How much can data center contribute?
Notes: ----- Meeting Notes (10/16/15 13:52) -----
currently (DR) are distributed, using them alone is difficult to satisfy DR needs,
some suggestions: how to find DR resources?

## Slide 5: Data centers have great potential for DR
20 MW Data Center with 20% flexibility
700 kWh fast charging, optimally placed storage
[Liu et al 2014]
This talk: Efficient DR in Multi-tenant Data Centers
However, current participation is still inefficient
~$5 million cost!
Notes: we live in an age of mobile computing where a lot of computation and storage is offloaded to the cloud, which are data centers, as a result, we can see the graph on the left showing a rapid increase in the,
studied shown that a data center 20MW has the potential to offer ancillary service to the power system via demand response that is of optimally place storage that is worth 5 million,
we can do the math …
massive potential social benefit -> we should understand how to do this efficiently -> but first we need to understand better what are (the typical) data centers

## Slide 6: Multi-tenant (colocation) data centers
Multiple tenants house and manage their own servers independently in shared space
Notes: they own the servers, pay subscription for electrcity and cooling

## Slide 7: Multi-tenant (colocation) data centers
Multiple tenants house and manage their own servers independently in shared space
Data center operator is mainly responsible for facility support (e.g., power supply, cooling)
Utility Substation
Diesel Generator
PDU
UPS
AC/DC
DC/AC
ATS
Tenants
Operator
Notes: they own the servers, pay subscription for electrcity and cooling

## Slide 8: Multi-tenant (colocation) data centers
Multiple tenants house and manage their own servers independently in shared space
Data center operator is mainly responsible for facility support (e.g., power supply, cooling)
Chart: 
| Traditional Enterprise | Multi-Tenant Colocation (e.g., Equinix) | Hyper-Scale Cloud Computing (e.g., Google) | High-Performance Computing (e.g., DOE)
Estimated Energy Usage by U.S. Data Center Segment in 2011 | 53 | 37.3 | 7.8 | 1.9
CoreSite’s “One Wilshire” (Photo: CoreSite)
Hyper-scale (e.g. google): 7.8%
Enterprise: 53%
Colocation: 37%
…of total data center industry electricity usage
Notes: they own the servers, pay subscription for electrcity and cooling
----- Meeting Notes (10/16/15 14:19) -----
color contrast of the pie chart

## Slide 9: Why target multi-tenant data center for DR?
Most multi-tenant data centers are in metropolitan areas
Downtown Los Angeles, New York, Silicon Valley, etc.
This is where demand response is most needed!
CoreSite’s “One Wilshire” (Photo: CoreSite)
Example: On July 22, 2011, hundreds of multi-tenant colocation data centers participated in emergency demand response and contributed by cutting their electricity usage before a nation-wide blackout occurred in the U.S. and Canada.
--- A. Misra, “Responding Before Electric Emergencies.”

## Slide 10: How do multi-tenant data center provide DR?
  Turn on diesel generator upon utility’s request
    Costly and environmentally unfriendly
Opportunity:
Tenants typically have great flexibility in energy usage
We should buy energy reduction from tenants!
[LBNL,HP] workload management can save 10-30+% in server energy 10-60min
Notes: we need to do better, it is not hard to see that this solution is suboptimal because it is not using the flexibility of workload to reduce server consumption energy
----- Meeting Notes (10/16/15 14:19) -----
talk about (change the graph) - currently the power system is incentive the customer to do demand response (we can do the similar thing), but this is a really challenging problem which Im going to show in a few slides

## Slide 11: Our contribution: a simple and provably efficient mechanism to incentivize tenants’ reduction
cost of local generation
cost of load reduction
meets energy reduction target
Operator’s challenge:
No direct control of tenants’ reduction si
Tenants’ private cost ci unknown
Goal:
y: amount of local generation α: price for diesel
si: load reduction of tenant i ci: cost of reduction of tenant i
Notes: ----- Meeting Notes (10/16/15 14:19) -----
flip 1 and 2,
first uncontrollable, even controllable, ...

## Slide 12: ColoDR: a supply function mechanism for DR
Operator
Tenants
Utility
Cut energy δ
Cut energy by
si=δ-bi/p
Operator announces supply function s(b, p) = δ-b/p
Tenant i submits bid bi
Operator sets market price p to minimize it own cost (payment to tenants plus diesel cost)
DR is exercised
Diesel energy
y = δ - Σisi
Price p
Supply bid bi
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/16/15 14:19) -----
explain what is supply function
for each price how
bid reflects tenants unwillingness to reduce
the process is to get flexibility from the tenants through bidding

## Slide 13: ColoDR: a supply function mechanism for DR
Operator
Tenants
Utility
Cut energy δ
Cut energy by
si=δ-bi/p
Diesel energy
y = δ - Σisi
Price p
Supply bid bi
Simple: tenant only need to communicate one parameter
Fair: no price differentiation
Cost saving for operator: cost of dispatch decrease compared to diesel only
Equilibrium: always exists and unique(more on this later)
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/16/15 14:19) -----
explain what is supply function
for each price how
bid reflects tenants unwillingness to reduce
the process is to get flexibility from the tenants through bidding

## Slide 14: Why supply function bidding?
VCG type mechanisms are problematic
  [Zhang et al 2015] [Rothkopf 2007]
Supply function bidding is widely used in electricity market
  [Baldick et al 2004] [Day et al 2002] [David and Wen 2000]
Prior work on supply function bidding
  [Klemperer and Meyer 1989] [Niu et al 2005] [Johari and Tsitsiklis 2011] [Xu et al 2015]
Notes:     Complex bidding process
    Differentiated price
    Expose private information
    Unbounded payment
----- Meeting Notes (10/15/15 12:54) -----
reorder 2 1 3
list the problem of VCG
add by text difference
spend more time on this slide
----- Meeting Notes (10/16/15 14:19) -----
not emphasize privacy too much, talk about pricing

## Slide 15: How well does ColoDR work?
What is the social cost?
What are tenants’ costs?
What is operator’s cost?
What is the reduction in diesel usage?
We answer these questions with both theoretical guarantees and trace-based simulations
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy

## Slide 16: What should we compare to?
Benchmark: Centrally controlled social cost minimization (SCM)
Tenant behavior for ColoDR
  Price-taking: Consider the price as is:
  Price-anticipating: Consider the impact of bidding decisions on the market price:
Notes: ----- Meeting Notes (10/9/15 12:56) -----
explain setting where taking vs anticipating occurs

## Slide 17: What should we compare to?
Case study
DR signals issued by PJM on January 7, 2014, due to cold weather.
Three different types of workload with different tolerance to delay.

## Slide 18: 1. What is the social cost?
Theorem: For both price-taking and price-anticipating tenants,
Vanishing when N is large,
what if N is small?
Near optimal when N is small
 ColoDR(price-taking) ColoDR(price-anticipating) SCM Diesel-only
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/15/15 12:54) -----
add the difference between price-taking and price-anticipating, spend more time explaining the figures
----- Meeting Notes (10/16/15 14:19) -----
talk about axis meanings

## Slide 19: 2&3. What are tenants’ and operator’s costs?
Operator have
lower cost than SCM
Theorem: For both price-taking and price-anticipating tenants,
Higher utility for tenants with larger flexibility
 ColoDR(price-taking) ColoDR(price-anticipating) SCM Diesel only
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy

## Slide 20: 4. What is the reduction in diesel usage?
Theorem: For both price-taking tenants,
for price-anticipating tenants,
In worst case, ColoDR may use a lot
more diesel than optimal
 ColoDR(price-taking) ColoDR(price-anticipating) SCM
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/16/15 14:19) -----
move on more quickly to emphasize the first set of result

## Slide 21: How well does ColoDR work?
What is the social cost?
What is tenants’ cost?
What is operator’s profit?
What is the reduction in diesel usage?
All these follow from one key characterization lemma
Notes: ----- Meeting Notes (10/16/15 14:19) -----
change profit to cost

## Slide 22: A characterization lemma
Characterize equilibrium as the outcome of an optimization problem
Lemma: When tenants are price-taking, the market equilibrium is unique and characterized by
Due to strategic behavior of operator

## Slide 23: A characterization lemma
Characterize equilibrium as the outcome of an optimization problem
Lemma: When tenants are price-anticipating, the market equilibrium is unique and characterized by
where
Strategic behavior of operator
Strategic behavior of tenants

## Slide 24: Two messages
#1: Multi-tenant data center DR is a billion dollar market
  Turning an energy hog into a social asset!
#2: Multi-tenant data center demand response can be “green” by incentivizing tenants’ cooperation
  Our proposed mechanism based on supply function bidding incentivizes and coordinates tenants’ energy shedding, with a provably-efficient outcome.
Notes: 1. doing DCDR efficiently and in an environmentally

## Slide 25
Backup Slides

## Slide 26: Who are using colocations?
Almost all industry sectors
  Including top-brand websites, e.g., Wikipedia, Twitter
Many clouds
Our Internet
  According to Cisco, 55% Internet traffic will be processed through CDN providers, e.g., Akamai, by 2018 (up from 33% in 2013)

## Slide 27: How do capacity constrained tenant bid bi?
We know that operator will not offer a price higher than α
Suppose tenant i cannot reduce load by more than K
With no information about how other tenants behave
  start bidding bi ≥ α(δ-K)
  load reduction si = δ– bi/p ≤ δ-bi/α ≤K
  adjust bid according to result of interaction in the mechansim

## Slide 28: How do operator decides price p?
minimize cost of DR
  min p(δ-y) + αy
Given bi and y,
Σi si + y = Σi (δ-bi/p) + y = δ, p = Σi bi / ((N-1)δ+y)
Operator solves the following problem

## Slide 29: Why does colocation matter?
There’re over 1,400 colocation data centers in the U.S.
Projected to grow to US$ 43 billion by 2018*
  Annual compound growth rate of 11%
www.datacentermap.com
* Source: http://www.marketsandmarkets.com/Market-Reports/colocation-market-1252.html

## Slide 30: In fact…
“Most large data centers are built to host servers from multiple companies (often called colocation data centers, or ‘colos’).”
    --- The Datacenter as a Computer, a study by Google Research in 2013

## Slide 31: Emergency demand response
Reduce energy to a certain level during emergencies
The last line of protection against grid-wide blackouts to avoid billions of dollars’ loss
Participation is booming
  e.g., PJM Interconnection
www.pjm.com

## Slide 32: ColoDR: a supply function mechanism for DR
Operator
Tenants
Utility
Price p
Cut energy δ
Diesel energy
y = δ - Σisi
Supply bid bi
Cut energy by
si=δ-bi/p
Operator announces supply function s(b, p) = δ-b/p
Tenant i submits bid bi
Operator sets market price p to minimize it own cost (payment to tenants plus diesel cost)
DR is exercised
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/16/15 14:19) -----
explain what is supply function
for each price how
bid reflects tenants unwillingness to reduce
the process is to get flexibility from the tenants through bidding

## Slide 33: ColoDR: a supply function mechanism for DR
Operator
Tenants
Utility
Price p
Cut energy δ
Diesel energy
y = δ - Σisi
Supply bid bi
Cut energy by
si=δ-bi/p
Simple: tenant only need to communicate one parameter
Fair: no price differentiation
Cost saving for operator: cost of dispatch decrease compared to diesel only
Equilibrium: always exists (more on this later)
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/15/15 12:54) -----
equilibrium always exists and unique

## Slide 34: ColoDR: a supply function mechanism for DR
Operator
Tenants
Utility
Price p
Cut energy δ
Diesel energy
y = δ - Σisi
Supply bid bi
Cut energy by
si=δ-bi/p
Simple: tenant only need to communicate one parameter
Fair: no price differentiation
Cost saving for operator: cost of dispatch decrease compared to diesel only
Equilibrium: always exists (more on this later)
Notes: ----- Meeting Notes (10/9/15 12:56) -----
this function indicates that for a price p, tenant will be offering s reduction specified by this equation, more constraint the tenant is, b specified the inconvenience incurred by the tenant to reduce energy
----- Meeting Notes (10/15/15 12:54) -----
equilibrium always exists and unique